| GDA Regulatory Observation |  |
| --- | --- |
| REGULATOR TO COMPLETE |  |
| RO unique no.: | RO-RRSMR-010 |
| Revision: | 1 |
| Date sent: | 02/07/2025 |
| Acknowledgement required by: | 06/08/2025 |
| Resolution Plan Agreement Required by: | 03/09/2025 |
| Record Reference: | ONRW-2126615823-7765 |
| Related RQ / RO No. and CM9 Ref: (if any): | RQ-01552 RQ-02048 RQ-02207 |
| Observation title: | Demonstration of the appropriate power rating and performance capability of the Electrical Power System |
| Lead technical topic: Electrical Engineering | Related technical topic(s): Control & Instrumentation External Hazards Fault Studies Internal Hazards Mechanical Engineering Severe Accident Analysis |
| REGULATORY OBSERVATION: |  |
| Background Electrical Power Systems (EPS) are important to Nuclear Power Plants (NPP) in providing both the sources of electrical energy and then distributing that energy to safety equipment that delivers the various safety functions to bring the NPP to a controlled and then safe shutdown state. ONR’s “Generic Design Assessment Technical Guidance” [1] provides specific guidance on the aspects of electrical engineering that ONR would expect to assess as part of GDA. This includes “a computer based model should be established by the RP [Requesting Party] for the purpose of studying the system under steady state conditions and in response to a range of postulated disturbances which can challenge the system performance. The studies should consider all modes of operation including normal operation, plant shutdown, on line plant maintenance, testing of standby sources and operation from standby sources…The results of the studies should be assessed to confirm compliance with pre-defined acceptance criteria.” ONR has reinforced this regulatory expectation with Rolls-Royce SMR Ltd, the Requesting Party (RP), that electrical system studies should be undertaken ensuring they “demonstrate the adequacy of the design” and be using the “fault scenarios and associated electrical loading sequences to inform electrical analyses”. As part of the agreed Step 3 submission schedule, the RP has submitted the initial set of documents to fulfil the analysis [2]. Those submissions do not give sufficient explanation of the process or analysis of the system sizing or performance for ONR to have confidence that the EPS is adequately designed to perform as required by the E3S case. ONR is concerned that the RP has not clearly presented the system models or the design data used throughout the studies in a manner which allows it to have confidence that the models adequately reflect the EPS or that the modelling data adequately represents the equipment parameters of Systems, Structures and Components (SSC). The choices or assumptions made in the development of the model or defining equipment characteristics are not consistently presented or justified. This lack of clarity continues with the selection of conditions for study, where aspects such as the modes of operation, fault sequences and limiting conditions of operation in the development of bounding cases are not clearly presented or justified. The acceptance criteria for studies are not consistently identified or linked to requirements in the safety case, which results in inadequate demonstration of the design or identification of gaps, and appropriate actions to mitigate those gaps. Finally, in the documents submitted to date, there are a number of areas where the results do not meet the RP’s own acceptance criteria. As a result, a fundamental expectation of [1] that “the results of the studies should be assessed to confirm compliance with pre-defined acceptance criteria” has not been met and it is therefore not being demonstrated that the electrical system is appropriately designed to fulfil its safety role or be operable in a safe manner. A Regulatory Query (RQ) [3] has been raised to seek clarity on individual aspects of submissions to date that has highlighted that the gaps are unlikely to be fully addressed through clarification provided in the responses to the RQs. This Regulatory Observation has therefore been raised to ensure that there is a robust demonstration of the adequacy of the EPS to distribute electrical power in all operating modes and in the presence of a range of postulated disturbances. Relevant Legislation, Standards and Guidance EPS provide an essential support function in supplying electrical power to safety functions. A reliable power supply is critical for maintaining control during normal operations, anticipated deviations from normal operation, as well as to power, control and monitor relevant plant safety functions in design basis accidents and design extension conditions. This importance is reflected in a number of standards and guidance documents, both international and national. Requirement 41 of IAEA Specific Safety Requirement SSR-2/1 (Rev.1) [4] reflects this expectation: “The functionality of items important to safety at the nuclear power plant shall not be compromised by disturbances in the electrical power grid, including anticipated variations in the voltage and frequency of the grid supply.” This is further reflected in many of the sections of the IAEA Specific Safety Guide for Electrical Power Systems SSG-34 [5]. For example, Paragraph 2.19 identifies the need to consider margins and conservatisms in the design whilst Section 4 outlines the need to identify and consider the design bases, all operational states, all modes of operation and all possible events in the analysis. BE EN IEC 63046:2021 [6] establishes the “high level specification requirement to implement a suitable Electrical Power System in a NPP that supports reactor systems important to safety.” It sets out the importance of ensuring “the electrical design of the Electrical Power System shall be verified” and that such verification should be “carried out and documented at each step of the design”. It recognises the importance of applying a ‘margin strategy’ to the electrical system studies “to cover modification during the NPP project design phase”. BS EN IEC 62855:2021 [7] specifically supports the guidance of [5, 6] and provides “guidelines for the analysis of AC and DC electrical power systems in NPPs in order to demonstrate that the power sources and the distribution systems have the capability for safe operation and shutdown of the NPP, bringing it to a controlled state after an anticipated operational occurrence or accident conditions and finally reaching a safe state.” It sets out that these “Analytical studies validate the robustness and adequacy of design margins and demonstrate the capability of electrical power systems to support plant operation for normal, abnormal, degraded and accident conditions” whilst “During the design stage of on-site power system, spare capacity for future load growth and uncertainties in the final parameters of proposed safety loads should be considered in the sizing criteria.” Three principles from ONR Safety Assessment Principles (SAP) for Nuclear Facilities [8] provide focus of the expectations in this area: - SAP EES.3 expects that “each source should have the capacity, duration, availability, resilience and reliability to meet the maximum demands of its dependent systems.” - SAP ESS.10 expects that “the capability of a safety system, and of each of its constituent sub-systems and components, should be defined and substantiated.” - SAP ESS.11 expects that “the adequacy of the system design as the means of achieving the specified function and reliability should be demonstrated for each system.” ONR’s Technical Assessment Guide on Essential Services TAG-019 [9] provides supporting guidance. It states that: - “The purpose of the [ONR] assessment is to confirm, with regard to essential services, that the licensee can demonstrate that they possess the relevant attributes commensurate with the safety significance including capacity, duration, availability, resilience and reliability”; - “The SSC capability should exceed that necessary for the effective delivery of the safety functions in the prevailing operating environment by a clear margin (ESS.10)”; and - “Each electrical supply source should have the capacity, duration, availability, resilience and reliability to meet the maximum demands of its dependent systems (EES.3). Electrical analysis should be carried out to ensure that the electrical supply, generators and distribution networks are capable of delivering the maximum electrical loading requirements and to determine system resilience to faults and disturbances.” Regulatory Expectations The above section shows that the expectation that the EPS is shown to be appropriately sized and resilient to faults and disturbances is, therefore, not only reflected in ONR’s TAG [9] but also in an IAEA Safety Guide [5] and International Standards [6, 7]. ONR considers that demonstrating the appropriate rating of equipment and then confirming through analysis that the equipment responds appropriately to load sequences and plant transients is a vital aspect in validating the electrical engineering aspects of a safety case. By doing this, the studies should demonstrate the ability of the EPS to continue to support the necessary safety functions. If the analysis does not do this, then it is no longer clear that the EPS would be able to support the necessary safety functions, when required. ONR’s regulatory expectation is that the RP should establish a robust method for determining the ratings of electrical equipment comprising the EPS, ensuring that such equipment can operate under all postulated conditions, taking conservative decisions where uncertainty may exist. ONR expects that the RP should then demonstrate the adequacy of the RR SMR EPS through the development of a system model and the undertaking of analytical studies of the system under both steady state conditions and in response to a range of postulated disturbances, which could challenge the ability of the system to support the necessary safety functions. It is expected that such studies should consider all modes of operation including normal operation, plant shutdown, including in response to plant faults, on-line plant maintenance, testing of standby sources and operation from standby sources. Where uncertainty could exist in the modelling, system data and parameters, or performance requirements, ONR expects a conservative but consistent approach be adopted in the sizing and studies, using, as appropriate, sensitivity analysis to give confidence that the uncertainties do not mask potential design shortfalls, which may not otherwise become apparent until later in the detailed design, construction or operational phase. ONR expects that the results of any analyses are evaluated by the RP against pre-defined acceptance criteria developed from safety case requirements or relevant requirements or good practice. Where such evaluation does not demonstrate analysis, it is expected that the RP should identify and evaluate appropriate changes to the design. References [1] ONR, New Nuclear Power Plants: Generic Design Assessment Technical Guidance, Revision 0, May 2019, ONR-GDA-GD-007. https://onr.org.uk/media/c2delysl/onr-gda-007.pdf [2] Requesting Party Electrical Power System Study Reports - Rolls-Royce SMR Ltd, Electrical Power System Studies Methodology Report, SMR0015613, Issue 1, October 2024 (Record ref. ONRW-2019369590-14384) - Rolls-Royce SMR Ltd, Electrical Power System Studies – Bounding Scenarios & Acceptance Criteria, SMR0021038, issue 1, April 2025 (Record ref. ONRW-2019369590-19392) - Rolls-Royce SMR Ltd, Electrical Power System Studies – Input Data Schedule Workbook, SMR0021030, Issue 1, March 2025 (Record ref. ONRW-2019369590-19259) - Rolls-Royce SMR Ltd, Overall Electrical Load Schedule, SMR0000975, Issue 5, March 2025 (Record ref. ONRW-2019369590-19262) - Rolls-Royce SMR Ltd, Electrical Power System Studies – Short Circuit Analysis Study Report, SMR0022256, Issue 1, April 2025 (Record ref. ONRW-2019369590-20238) - Rolls-Royce SMR Ltd, Electrical Power System Studies – Motor Starting Study Report, SMR0022257, Issue 1, April 2025 (Record ref. ONRW-2019369590-20250) - Rolls-Royce SMR Ltd, Electrical Power System Studies – AC Load Flow & Power Balance Study, SMR0021039, Issue 1, May 2025 (Record ref. ONRW-2019369590-21243) - Rolls-Royce SMR Ltd, Electrical Power System Studies – House Load Operation Study Report, SMR0023400, Issue 1, May 2025 (Record ref. ONRW-2019369590-21242) [3] ONR Regulatory Queries relating to Electrical System Studies: - Electrical System Studies, RQ-01552 - Electrical System Studies – Derivation of Data and Bounding Cases, RQ-02048 - Electrical Power System Studies, RQ-2207 [4] Safety of Nuclear Power Plants: Design. Specific Safety Requirements No SSR-2/1, Rev. 1, IAEA, February 2016. www.iaea.org [5] Design of Electrical Power Systems for Nuclear Power Plants, Specific Safety Guide SSG-34, IAEA, March 2016. www.iaea.org [6] Nuclear power plants – Electrical power systems – General requirements, BS EN IEC 63046:2021, British Standards Institution. www.bsigroup.com [7] Nuclear power plants – Electrical power systems – Electrical Power systems analysis, BS EN IEC 62855:2021, British Standards Institution. www.bsigroup.com [8] Safety Assessment Principles for Nuclear Facilities. 2014 Edition Revision 1, ONR, January 2020. www.onr.org.uk/media/pobf24xm/saps2014.pdf [9] Essential Services – Technical Assessment Guide, NS-TAST-GD-019 Revision 4, ONR, July 2019 http://www.onr.org.uk/operational/tech_asst_guides/index.htm |  |
| REGULATORY OBSERVATION ACTIONS |  |
| RO-RRSMR-010.A1 – Develop an appropriate Rolls-Royce SMR Electrical Power System Sizing and Study Strategy In response to this Regulatory Observation Action, Rolls-Royce SMR Ltd should: - Develop a strategy to establish the rating of electrical power supply (EPS) equipment and analyse the Rolls-Royce SMR EPS against anticipated events and disturbances. The strategy should seek to: - Identify and justify how it is intended to structure the electrical system model(s) and analyse the EPS; - Identify how it is intended to demonstrate the verification and validation of any analytical tools (such as software) or methods it intends to use to support its analysis; - Identify and justify any assumptions to be made in the development of the model, underlying System, Structures and Components (SSC) parameters, and intended analysis; - Identify and justify the different ‘study conditions’ that it is intended to analyse; (The term “study condition” is used here to include, but not limited to, modes of operation, plant configurations, fault scenarios and environmental conditions) - Identify and justify the identification of any ‘bounding cases’ that are used to reduce the number of study conditions; and - Identify the acceptance criteria for each of the studies, explaining how these have been derived from the safety case requirements. In developing the strategy, the RP should consider: - How it is ensuring that where it uses different software or different models for different studies, it demonstrates that the representations of the EPS remain consistent and do not compromise any assumptions or the study results; - How it is demonstrating it is adopting a conservative, but reflective, approach when considering the design maturity of the overall Rolls-Royce SMR design, SSC parameters and the supporting analysis; and - How in defining the “study conditions” it is showing traceability from the fault and hazard analyses. Resolution required by 'to be determined by Rolls-Royce SMR Limited Resolution Plan' |  |
| RO-RRSMR-010.A2 – Analyse the Rolls-Royce SMR Electrical Power System In response to this Regulatory Observation Action, Rolls-Royce SMR Ltd should: - Using the strategy developed in response to RO-RRSMR-010.A1: - Develop the system model(s); - Determine the minimum electrical ratings of the EPS equipment; - Analyse the performance of the EPS in response to the identified “study conditions”; and - Analyse the results against the acceptance criteria, identifying any gaps against the extant safety case and system design. In undertaking the sizing and analysis, the RP should consider: - The justification for any changes to the assumptions or acceptance criteria that have been necessary during the sizing or analyses; - How any such changes do not undermine the results or conclusions of any other analyses or the design; and - The sensitivity of the analysis findings to uncertainties in the model data or assumptions. Resolution required by 'to be determined by Rolls-Royce SMR Limited Resolution Plan' |  |
| RO-RRSMR-010.A3 – Identify and manage any gaps resulting from the analysis of the Rolls-Royce SMR Ltd Electrical Power System In response to this Regulatory Observation Action, Rolls-Royce SMR Ltd should: - Based on the completion of the analysis undertaken in response to RO-RRSMR-010.A2: - Identify the implications for any shortfalls against the extant safety case arising from the system studies; - Undertake optioneering studies to identify appropriate solutions to address those shortfalls; - Explain the implications of any modifications on the safety case, including the impact on the EPS design and the other electrical system studies; and - Explain how those modifications could be implemented and the Rolls-Royce SMR GDA safety case updated. Resolution required by 'to be determined by Rolls-Royce SMR Limited Resolution Plan' |  |

| REQUESTING PARTY TO COMPLETE |  |
| --- | --- |
| Actual Acknowledgement date (dd/mm/yy): |  |
| RP stated Resolution Plan agreement date (dd/mm/yy): |  |